Appendix 1 Template for cooling tower system risk management plan

Components and format of a risk management plan

Generally, a risk management plan (RMP) should have a number of basic components, including:

•
site and contact details

•
assessment of each of the critical risks

•
summary of the overall risk classification

•
details of the system (collected during the risk assessment process)

•
attachments or references to other documents, such as operational plans and shut-down procedures.

There is no prescribed format for an RMP. This template is provided as a guide, but other formats may be used.
About the template

The template is designed to be completed:

•
by operators of cooling tower system, or landowners who have cooling tower systems on their land

•
after reading this guide

•
after completing a thorough risk assessment, as outlined in this guide.

This process will meet the requirements of the Public Health and Wellbeing Act 2008 for development of an RMP.

An RMP must be developed for every cooling tower system on the site. It must be made available to an authorised officer of the Department of Health and Human Services on request.

Implementation of the operational program outlined in the RMP would also meet the requirements of the Public Health and Wellbeing Regulations 2009.

An electronic version of the template (in Word) is also available,
 and can be modified for development of an RMP.

	Disclaimer

This document is intended only as a general guide to the development of risk management plans for cooling tower systems. No warranty as to the completeness of the information is given. The Department of Health and Human Services and its employees disclaim all liability and responsibility for any direct or indirect loss or damage that may be suffered through reliance on any information contained in, or omitted from, this document. No person should act solely on the basis of the information contained in the document without obtaining appropriate professional advice about obligations in specific circumstances.


Site and key contact details

	Record
	Details

	Site location (property address)
	

	Number of cooling towers in system
	

	Cooling tower system number17
	

	Registration period18
	

	Tower location reference (if one exists)
	

	Site owner’s name and contact details (Include company name, and contact person’s business and after-hours telephone numbers)
	

	Cooling tower system owner’s name and contact details
(Include company name, and contact person’s business and after-hours telephone numbers)
	

	Person responsible for day-to-day operation of the cooling tower system (Include company name, and contact person’s business and after-hours telephone numbers)19
	

	Water treatment provider’s name and contact details (Include company name, and contact person’s business and after-hours telephone numbers)
	

	Water sampling or laboratory contractor name and contact details (Include company name, and contact person’s business and after-hours telephone numbers)
	

	Department of Health and Human Services Legionella Team
	1800 248 898


Critical risks

Stagnant water

	Risk control strategy for stagnant water
	Assessment of the cooling 
tower system
	Operational or tower system improvement response20

	Install a timer connected to a recirculating pump set to operate at least once a day to circulate the water
	Is the system (or part of the system) idle for more than a month?

 Yes
 No
	

	
	Where the system (or part of the system) is idle for more than a month, is a recirculating pump with a timer fitted to automatically circulate the water at regular intervals, to prevent it becoming stagnant?

 Yes
 No21
	

	Remove or activate any ‘dead legs’
	Are there dead legs in the system?

 Yes
 No
	

	Other22
	
	


	Risk classification for stagnant water23 
 A
 B
 C
 D


Nutrient growth

	Risk control strategy for nutrient growth
	Assessment of the cooling 
tower system
	Operational or tower system improvement response24

	Identify sources of environmental contamination and, where possible, reduce the amount of contamination
	Are there factors in and around the site that may lead to environmental contamination and an increase in the level of nutrients in the water of the cooling tower system?

 Yes
 No
	

	
	If ‘Yes’, can you reduce the levels of contamination?

 Yes25
 No26
	

	Control corrosion
	Do you have a corrosion control program?

 Yes
 No27
	

	Increase the frequency of cleaning
	How frequently is the tower cleaned?28
	

	Protect the basin and ‘top deck’ of the tower from sunlight
	Are any of the wetted surfaces exposed to sunlight?

 Yes29
 No
	

	Reduce the water temperature, where possible
	Can the water temperature of the tower be reduced?

 Yes30
 No31
	

	Other32
	
	


	Risk classification for nutrient growth33
 A
 B
 C
 D


Poor water quality

	Risk control strategy for poor water quality
	Assessment of the cooling 
tower system
	Operational or tower system improvement response34

	Ensure comprehensive water treatment program
	Do you use two or more biocides in some form of rotation?

  Yes
 No35
	

	
	Is the system continuously treated with a biodispersant?

 Yes
 No36
	

	
	Do you use a biodispersant that is compatible with the other chemicals in use (including chlorine) during the disinfection, cleaning and re-disinfection process?

 Yes
 No37
	

	
	Do you treat the water with anticorrosion chemicals?

 Yes
 No38
	

	
	Have you developed performance indicators that are frequently measured to confirm that the water chemistry is under control?

 Yes39
 No40
	

	Test for HCC
	How frequently do you test for HCC?
	

	Test for Legionella
	How frequently do you test for Legionella? 41
	

	Manage HCC
	What HCC do you allow before you take remedial action?

 200,000 CFU/mL

 Less than 200,000 CFU/mL42
	

	Respond to high HCC results
	How do you respond to a high HCC test result?

 We follow Figure A143
 We follow Figure A244
 We follow our own response plan45
	

	Respond to the detection of Legionella
	How do you respond to Legionella being detected in a sample?46
 We follow Figure A347
 We follow another plan that still meets the requirements of the Regulations48
	

	Respond to the detection of Legionella on two or more occasions within a 12-month period
	How do you respond to Legionella being detected in a sample on two or more occasions during a 12-month period49?

 The RMP is reviewed, in addition to the required actions (refer to Figure A3)

 Other (provide details)
	

	Label the cooling tower system
	Is the cooling tower and cooling tower system labelled with the CTS number?

 Yes50
 No51
	

	Ensure appropriate bleed-off rates to prevent a build-up of solids
	Is an automated bleed-off device installed?52
 Yes
 No53
	

	Install automated biocide dosing device
	Do you have an automated biocide dosing device?
 Yes
 No54
	

	Install automated dosing devices for all chemicals and agents
	Do you have automated dosing devices for all chemicals and agents?

 Yes
 No55
	

	Select an appropriate point for chemical dosing
	Does the chemical dosing occur well away from the sampling point for bacterial tests?

 Yes
 No56
	

	Provide a dedicated water sampling point
	Are water samples always taken from the same point?

 Yes
 No
	

	
	If ‘Yes’, is that point clearly labelled with the CTS number?57
 Yes
 No
	

	
	Has a sampling tap been fitted?

 Yes
 No
	

	Install a side-stream filter if environment is dirty
	Is the environment around the tower dirty?

 Yes
 No
	

	
	If ‘Yes’, do you have a side-stream filter?

 Yes
 No58
	

	Other59
	
	


CFU = colony forming unit; CTS = cooling tower system; HCC = heterotrophic colony count

	Risk classification for poor water quality60
 A
 B
 C
 D


Deficiencies in the cooling tower system

	Risk control strategy for deficiencies in the cooling tower system
	Assessment of the cooling 
tower system
	Operational or tower system improvement response61

	Review the system design against AS/NZS 3666
	Has a review been conducted?

 Yes
 No62
	

	
	Can any improvements be made to the system design to reduce risks?

 Yes63
 No64
	

	Review current performance of system
	Has a review been conducted?

 Yes65
 No66
	

	Develop operating and maintenance manuals
	Have operating and maintenance manuals been developed?

 Yes
 No67
	

	Review the useful life of the system and plan to replace it at an appropriate time
	When was the tower built?
	

	
	Do you have a program to replace it?

 Yes68
 No69
	

	Install a modern, high-efficiency drift eliminator
	Is a modern, high-efficiency drift eliminator fitted to every tower in the system?

 Yes
 No70
	

	
	Are the drift eliminators in good condition?

 Yes
 No71
	

	
	Have the drift eliminators been certified by the manufacturer as meeting AS/NZS 3666?

 Yes
 No72
	

	Use suitable materials for external components
	Have you reviewed the condition of the tower structure?

 Yes73
 No74
	

	Use suitable materials for internal components
	Have you reviewed the materials and condition of the internal components of the tower system?

 Yes75
 No76
	

	Other77
	
	


	Risk classification for deficiencies in the cooling tower system78
 A
 B
 C
 D


Location and access

	Risk control strategy for location and access
	Assessment of the cooling 
tower system
	Operational or tower system improvement response79

	Understand the extent of potential exposure to the cooling tower
	Is the cooling tower system located in an acute health or aged residential care facility?

 Yes80
 No
	

	
	If ‘No’, is the cooling tower system located within 500 m of an acute health or aged residential care facility?

 Yes81
 No
	

	Minimise access to tower and surrounds
	How many people have access to the tower and its surrounds?82
 Very high numbers83
 High numbers84
 Moderate numbers85
 Low numbers86
	

	
	Are warning signs87 displayed around the tower?

 Yes
 No88 
	

	
	Is the area around the cooling tower system used as a gathering place for staff and visitors, particularly smokers?

 Yes89
 No
	

	
	Is access to the tower restricted?

 Yes
 No90
	

	Relocate the tower to a more remote site or less contaminated environment (where possible)
	Have you reviewed whether it is possible to relocate the tower to a safer location?

 Yes91
 No92
	

	Ensure that there is a safe and stable area for maintenance workers to access the cooling tower system
	Have you reviewed the working environment for maintenance workers?93

 Yes94
 No95
	

	Other96
	
	


	Risk classification for location and access97
 A
 B
 C
 D


Risk assessment summary

	Critical risk
	Risk classification98

	Stagnant water
	 A
 B
 C
 D

	Nutrient growth
	 A
 B
 C
 D

	Poor water quality
	 A
 B
 C
 D

	Deficiencies in the cooling tower system
	 A
 B
 C
 D

	Location and access
	 A
 B
 C
 D

	Are there any other considerations that may affect the overall risk assessment of the cooling tower system?
	

	Overall cooling tower system risk classification category
	 A
 B
 C
 D


Attachments99

Operational program

Recommended operational programs based on risk classification

	Program A
	Program B
	Program C
	Program D

	Weekly inspection
	Monthly inspection (2 weeks after service)
	Monthly inspection (2 weeks after service)
	Monthly service

	Fortnightly service
	Monthly service
	Monthly service
	

	HCC and Legionella tested at a minimum of once each month
	HCC and Legionella tested monthly
	HCC tested monthly

Legionella tested every 2 months
	HCC tested monthly

Legionella tested every 3 months

	Six monthly cleaning, or more frequently where environmental contamination (e.g. dust, soil, building works) is a problem


HCC = heterotrophic colony count

	Element
	Response

	Describe your maintenance program
	 Department of Health and Human Services program A

	
	 Department of Health and Human Services program B

	
	 Department of Health and Human Services program C

	
	 Department of Health and Human Services program D

	
	 Self-developed

	
	 Developed by consultant

	If self-developed or developed by consultant, complete remainder of table

	Service frequency
	 Weekly

	
	 Fortnightly

	
	 Monthly

	HCC testing frequency
	 Monthly

 Every ………… week(s)

	Legionella testing frequency
	 Every 3 months
 Every ………… weeks/months

	Tower cleaning frequency
	 Every 6 months
 Every ………… months

	Inspection frequency
	 Every ………… weeks/months


Monitoring and review

	Element
	Response

	Date that the RMP is due for review
	

	Name and title of person responsible for the review
	

	Date that the RMP was reviewed
	

	Are all site and key contact details accurate? Has the Department of Health and Human Services been notified of any changes?
	 Yes
 No

	Is the cooling tower system currently registered with the Department of Health and Human Services?
	 Yes
 No

	Does the RMP require amendment?
	 Yes
 No

	Was the review conducted as a result of a triggering event?100
	

	If the RMP requires amendment, dates that the amendments were due and completed
	Due

	
	Completed


Communication

	Element
	Details

	List parties (names and contact details) who will be informed in the event of a positive Legionella test
	Category
	Name and title
	Telephone
	Comment

	
	Staff
	
	
	

	
	Occupational health staff or contractors
	
	
	

	
	Unions
	
	
	

	
	Building owner
	
	
	

	
	Other building occupiers
	
	
	

	
	Medical officer
	
	
	

	
	Staff counsellors
	
	
	

	
	Department of Health and Human Services Legionella Team
	
	1800 248 898 or email legionella@health.vic.gov.au
	

	
	Media liaison officer
	
	
	

	
	Company spokesperson
	
	
	

	
	Chief executive
	
	
	

	
	Other (specify)
	
	
	


Endorsement of risk management plan

	Name and position of person responsible for 
risk management plan
	

	Signature
	Date


� 	�HYPERLINK  "http://www.health.vic.gov.au/legionella/index"�www.health.vic.gov.au/legionella/index


�


� 	The Public Health and Wellbeing Act 2008 requires the department to be notified in writing within 30 days of any change in ownership, address or any other contact details by the owner of the land (or their agent) on which the cooling tower system is located.


17	This is marked on the Certificate of Registration supplied by the department.


18	The department registers cooling tower systems for 1, 2 or 3 years. The registration period is included on the certificate of registration.


19	This person has the authority to approve the disinfection of the system on request of the department. It is not the water treatment service provider.


�99 	Other information that can be appended to the RMP includes site plan, photographs, schematics of water flows, cooling tower makes and models, and basic system parameters (e.g. system volume, system heat rejection capacity, system operating temperature).





